Section 23 51 00

PART-1 BREECHING, CHIMNEY & STACKS

1:1 SCOPE

- Provide factory-built modular connector and/or vertical stack masonry chimney liner system that is tested and listed by the Underwriters’ Laboratories per the following:

  - ULC S635 (Standard for Lining Systems for Existing Masonry or Factory-Built Chimneys and Vents) for use with building heating equipment and appliances (gas, liquid, or solid fuel), which produce exhaust flue gases at a temperature not exceeding 1200°F (positive or negative pressures) under continuous operating conditions.

  - UL 1777 (Standard for Chimney Liners) for use with building heating equipment and appliances (gas or liquid fuel), which produce exhaust flue gases at a temperature not exceeding 570°F (positive or negative pressures) under continuous operating conditions.

  - The inner wall of a double wall UL 103 positive pressure chimney.

1:2 CONSTRUCTION

- The single wall flue system shall have a 304 (or 316) stainless steel inner liner (20 gauge min). The materials and construction of the modular sections and accessories shall be as specified by the terms of the product’s U.L. listing.

- Aluminized steel (20 gauge min) shall be used for general use ventilation (non-flue gas exhaust)

B. This vent system shall be designed and installed to prevent leakage of combustion products into a building.

C. Common pipe sections & fittings (ie; lengths/elbows/tees) shall have a self-centering sleeve to ensure proper alignment at the inner wall joint connection.

D. Pipe joints shall be securely connected and sealed with factory supplied overlapping V-bands and appropriate sealant as specified in the manufacturer’s installation instructions.

E. The vent system shall be designed and supported to compensate for all exhaust gas induced thermal expansion.

PART-2 EXECUTION

2:1 INSTALLATION

A. The prefabricated flue system shall be installed according to the manufacturer’s installation instructions, factory submittal drawing, and shall conform to all applicable state and local codes.

B. Provide all modular straight sections, fittings, supports, guides, expansion joints, roof thimbles, roof flashings, and terminations as required to provide a complete system per the manufacturer’s recommended design and installation instructions.

C. The entire flue system from the appliance outlet to the termination point, including all accessories, except as noted, shall be from one manufacturer.

D. The termination shall comply to local fuel gas code termination requirements and/or the heating appliance OEM’s requirements.

E. Roof penetrations shall be suitable for the specified roof construction and shall comply with the manufacturer’s installation instructions.

PART-3 WARRANTY

3:1 WARRANTY

A. The prefabricated flue system shall be warranted against functional failure due to defects in material and manufacturer’s workmanship for a period of 15 years from date of installation.

B. The inner diameter of the flue system shall be verified by the manufacturer’s venting computations. The computations used shall be technically sound, follow ASHRAE calculation methods and shall incorporate the specific flow characteristics of the inner pipe. The contractor shall furnish the exact operating characteristics of all equipment to the factory representative.

C. The manufacturer shall provide “to scale” drawings depicting the actual layout. The prefabricated flue system shall be installed as designed by the manufacturer and in accordance with the terms of the manufacturer’s warranty and in conjunction with sound engineering practices.

PART-4 PRODUCTS

4:1 MANUFACTURERS

A. Product specification requirements shall be met by using AMPCO Model N exhaust flue or equivalent as approved by the engineer. Equivalent submittals shall specify manufacturer’s model number, and other pertinent identification, and attest that the alternate material is in compliance with all specification requirements.

END OF SECTION 23 51 00